Copyright 2015 by The American Institute of Architects (AIA)

Exclusively published and distributed by AVITRU, LLC for the AIA

This Product MasterSpec Section is licensed by AVITRU, LLC to Armacell LLC ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Avitru or The American Institute of Architects (AIA). Neither AIA nor Avitru are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Armacell LLC, 55 Vilcom Center Drive, Suite 200, Chapel Hill, NC 27514; Phone: (984) 364-7433; Website: www.armacell.us; Email: thomas.j.mackinnon@armacell.com.

For information about MasterSpec, contact Avitru at (800) 424-5080 or visit avitru.com.

SECTION 230713 - DUCT INSULATION

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on MasterWorks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on MasterWorks/Supporting Information.

Content Requests:

<Double click here to submit questions, comments, or suggested edits to this Section.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section includes insulating the following duct services:

The list below matches the various systems in the schedule articles. Coordinate the revision of list with "Duct Insulation Schedule, General," "Indoor Duct and Plenum Insulation Schedule," and "Aboveground, Outdoor Duct and Plenum Insulation Schedule" articles.

          - Indoor, concealed supply and outdoor air.

          - Indoor, exposed supply and outdoor air.

          - Indoor, concealed return located in unconditioned space.

          - Indoor, exposed return located in unconditioned space.

          - Indoor, concealed, Type I, commercial, kitchen hood exhaust.

          - Indoor, exposed, Type I, commercial, kitchen hood exhaust.

          - Indoor, concealed oven and warewash exhaust.

          - Indoor, exposed oven and warewash exhaust.

          - Indoor, concealed exhaust between isolation damper and penetration of building exterior.

          - Indoor, exposed exhaust between isolation damper and penetration of building exterior.

          - Outdoor, concealed supply and return.

          - Outdoor, exposed supply and return.

        - Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 230716 "HVAC Equipment Insulation."

          - Section 230719 "HVAC Piping Insulation."

          - Section 233113 "Metal Ducts" for duct liners.

      - ACTION SUBMITTALS

        - Product Data: For each type of product indicated. Include thermal conductivity, water-vapor permeance thickness, and jackets (both factory- and field-applied if any).

        - Sustainable Design Submittals:

"Product Data" Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. Coordinate with requirements for adhesives.

          - Product Data: For adhesives, indicating VOC content.

"Laboratory Test Reports" Subparagraph below applies to LEED 2009 for Schools, LEED v4, IgCC, ASHRAE 189.1, and Green Globes. Coordinate with requirements for adhesives.

          - Laboratory Test Reports: For adhesives, indicating compliance with requirements for low-emitting materials.

"Product Data" Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. Coordinate with requirements for paints and coatings.

          - Product Data: For coatings, indicating VOC content.

"Laboratory Test Reports" Subparagraph below applies to LEED 2009 for Schools, LEED v4, IgCC, ASHRAE 189.1, and Green Globes. Coordinate with requirements for paints and coatings.

          - Laboratory Test Reports: For coatings, indicating compliance with requirements for low-emitting materials.

"Product Data" Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. Coordinate with requirements for sealants.

          - Product Data: For sealants, indicating VOC content.

"Laboratory Test Reports" Subparagraph below applies to LEED 2009 for Schools, LEED v4, IgCC, ASHRAE 189.1, and Green Globes. Coordinate with requirements for sealants.

          - Laboratory Test Reports: For sealants, indicating compliance with requirements for low-emitting materials.

        - Shop Drawings: Include plans, elevations, sections, details, and attachments to other work.

          - Detail application of protective shields, saddles, and inserts at hangers for each type of insulation and hanger.

          - Detail insulation application at elbows, fittings, dampers, specialties and flanges for each type of insulation.

          - Detail application of field-applied jackets.

          - Detail application at linkages of control devices.

Retain first paragraph below to verify products with Samples.

        - Samples: For each type of insulation and jacket indicated. Identify each Sample, describing product and intended use. Sample sizes are as follows:

          - Sheet Form Insulation Materials: 12 inches (300 mm) square.

          - Sheet Jacket Materials: 12 inches (300 mm) square.

          - Manufacturer's Color Charts: For products where color is specified, show the full range of colors available for each type of finish material.

      - INFORMATIONAL SUBMITTALS

Coordinate first paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as supplemented in "Quality Assurance" Article.

        - Qualification Data: For qualified Installer.

Retain first paragraph below if surface-burning characteristics specified in "Quality Assurance" Article are specified to be verified by an independent testing agency.

        - Material Test Reports: From a qualified testing agency acceptable to authorities having jurisdiction indicating, interpreting, and certifying test results for compliance of insulation materials, sealers, attachments, cements, and jackets, with requirements indicated. Include dates of tests and test methods employed.

Retain paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

      - QUALITY ASSURANCE

Retain first paragraph below if available at Project location. Apprenticeship programs are usually associated with union shops. Other craft training programs are available.

        - Installer Qualifications: Skilled mechanics who have successfully completed an apprenticeship program or another craft training program certified by the Department of Labor, Bureau of Apprenticeship and Training. Preference will be given to those who have successfully completed a manufacturer’s installation training program, such as the 'Armacell Qualified Installer Program' (AQIP) or similar.

        - Inspection: A certified mechanical insulation shall be performed by inspectors who maintain current certification, by the National Insulation Association or other certified mechanical association, throughout the project to inspect and verify the materials and the total insulation system has been installed correctly in accordance with the specifications and material manufacturer’s instructions.

When fire-performance characteristics are important requirements, verify surface-burning characteristics of insulation materials by an independent testing agency and require test report submittals.

        - Surface-Burning Characteristics: For insulation and related materials, as determined by testing identical products listed and labeled in accordance with UL 723 or tested in accordance with ASTM E 84, by a testing agency acceptable to authorities having jurisdiction. Factory label insulation and jacket materials and adhesive, mastic, tapes, and cement material containers, with appropriate markings of applicable testing agency.

          - Insulation Installed Indoors: Flame-spread index of 25 or less, and smoke-developed index of 50 or less.

          - Insulation Installed Outdoors: Flame-spread index of 75 or less, and smoke-developed index of 150 or less.

If retaining "Mockups" Paragraph below, indicate location, size, and other details of mockups on Drawings or by inserts. Revise if only one mockup is required.

        - Mockups: Before installing insulation, build mockups for each type of insulation and finish listed below to demonstrate quality of insulation application and finishes. Build mockups in the location indicated or, if not indicated, as directed by Architect. Use materials indicated for the completed Work.

          - Ductwork Mockups:

            - One 10-foot (3-m) section each of rectangular and round straight duct.

            - One each of a 90-degree mitered round and rectangular elbow, and one each of a 90-degree radius round and rectangular elbow.

            - One rectangular branch takeoff and one round branch takeoff from a rectangular duct. One round tee fitting.

            - One rectangular and round transition fitting.

            - Four support hangers for round and rectangular ductwork.

            - Each type of damper and specialty.

          - For each mockup, fabricate cutaway sections to allow observation of application details for insulation materials, adhesives, mastics, attachments, and jackets.

          - Notify Architect seven days in advance of dates and times when mockups will be constructed.

          - Obtain Architect's approval of mockups before starting insulation application.

Retain first subparagraph below if mockups are not only for establishing appearance factors.

          - Approval of mockups does not constitute approval of deviations from the Contract Documents contained in mockups unless Architect specifically approves such deviations in writing.

          - Maintain mockups during construction in an undisturbed condition as a standard for judging the completed Work.

          - Demolish and remove mockups when directed.

      - DELIVERY, STORAGE, AND HANDLING

Retain this article to require shipping container markings. Container marking is an option in ASTM standards; default condition does not include the marking in this article unless specified in the Contract.

        - Packaging: Insulation material containers shall be marked by manufacturer with appropriate ASTM standard designation, type and grade, and maximum use temperature.

      - COORDINATION

        - Coordinate sizes and locations of supports, hangers, and insulation shields specified in Section 230529 "Hangers and Supports for HVAC Piping and Equipment."

        - Coordinate clearance requirements with duct Installer for duct insulation application. Before preparing ductwork Shop Drawings, establish and maintain clearance requirements for installation of insulation and field-applied jackets and finishes and for space required for maintenance.

        - Coordinate installation and testing of heat tracing.

      - SCHEDULING

        - Schedule insulation application after pressure testing systems and, where required, after installing and testing heat tracing. Insulation application may begin on segments that have satisfactory test results.

        - Complete installation and concealment of plastic materials as rapidly as possible in each area of construction.

- PRODUCTS

      - INSULATION MATERIALS

If retaining more than one type of insulation in this article, indicate where each type applies in insulation system schedules.

        - Comply with requirements in "Duct Insulation Schedule, General," "Indoor Duct and Plenum Insulation Schedule," and "Aboveground, Outdoor Duct and Plenum Insulation Schedule" articles for where insulating materials shall be applied.

See "Product Characteristics" Article in the Evaluations for comparisons and temperature ranges for insulation material properties.

        - Products shall not contain asbestos, lead, mercury, or mercury compounds.

        - Products that come in contact with stainless steel shall have a leachable chloride content of less than 50 ppm when tested according to ASTM C 871.

        - Insulation materials for use on austenitic stainless steel shall be qualified as acceptable according to ASTM C 795.

        - Foam insulation materials shall not use CFC or HCFC blowing agents in the manufacturing process.

        - Flexible Elastomeric Insulation: Closed-cell, sponge- or expanded-rubber materials. Comply with ASTM C 534, Grade 1, Type II for sheet materials. UL Classified per UL 723 at 25/50.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

AP Armaflex is our standard product that meets 25/50 thru 1-inch (25-mm) thickness. AP Armaflex FS is our 1-1/2 inch- (38 mm-) thick and 2 inch- (51 mm-) thick sheet and roll that meets 25/50.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [ArmaFlex Ultra] [or] [ArmaFlex Ultra SA] or a comparable product by one of the following:

            - Aeroflex USA, Inc.

            - K-Flex USA.

            - <Insert manufacturer's name>.

        - Flexible Elastomeric Insulation: Closed-cell, sponge- or expanded-rubber materials. Comply with ASTM C 534, Grade 1, Type II for sheet materials.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

AP Armaflex is our standard product that meets 25/50 thru 1-inch (25-mm) thickness. AP Armaflex FS is our 1-1/2 inch- (38 mm-) thick and 2 inch- (51 mm-) thick sheet and roll that meets 25/50.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [AP ArmaFlex] [or] [AP ArmaFlex FS] or a comparable product by one of the following:

            - Aeroflex USA, Inc.

            - K-Flex USA.

            - <Insert manufacturer's name>.

        - Flexible Elastomeric Insulation: Closed-cell, sponge- or expanded-rubber materials with a self-adhering backing. Comply with ASTM C 534, Grade 1, Type II for sheet materials.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

AP Armaflex SA is our standard product with a self-adhering backing that meets 25/50 thru 1-inch (25-mm) thickness. AP Armaflex FS SA is our 1-1/2 inch- (38 mm-) thick and 2 inch- (51 mm-) thick sheet and roll, with a self-adhering backing, that meets 25/50.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [AP ArmaFlex SA] [or] [AP ArmaFlex FS SA] or a comparable product by one of the following:

            - Aeroflex USA, Inc.

            - K-Flex USA.

            - <Insert manufacturer's name>.

        - Flexible Elastomeric Insulation: Closed-cell, sponge- or expanded-rubber materials with a self-adhering backing. Comply with ASTM C 534, Grade 1, Type II for sheet materials.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

ArmaTuff is our insulation with a factory applied jacket. This is especially good for outdoor systems or areas of high-abuse. SA adds the self-adhering backing.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [ArmaTuff] [or] [ArmaTuff SA] or a comparable product by one of the following:

            - Aeroflex USA, Inc.

            - K-Flex USA.

            - <Insert manufacturer's name>.

        - Flexible Elastomeric Insulation: Closed-cell, sponge- or expanded-rubber materials. Comply with ASTM C 534, Grade 1, Type II for sheet materials.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

UT Solaflex is a high-temperature FEF with some UV resistance. It was made for solar applications. Maximum temperature of 300 deg F (149 deg C).

          - Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [UT Solaflex] or a comparable product by one of the following:

            - Aeroflex USA, Inc.

            - K-Flex USA.

            - <Insert manufacturer's name>.

For operating temperatures higher than 250 deg F (121 deg C), use blanket insulation in first paragraph below. Retain ASTM C 1290 types as follows: Type I for insulation without jackets and Type II for insulation with vinyl jackets, and Type III for insulation with FSK jackets.

        - Mineral-Fiber Blanket Insulation: Mineral or glass fibers bonded with a thermosetting resin. Comply with ASTM C 553, Type II and ASTM C 1290, [Type I] [Type II with factory-applied vinyl jacket] [Type III with factory-applied FSK jacket]. Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - CertainTeed Corporation.

            - Johns Manville; a Berkshire Hathaway company.

            - Knauf Insulation.

            - Manson Insulation Inc.

            - Owens Corning.

            - <Insert manufacturer's name>.

For operating temperatures higher than 250 deg F (121 deg C), use board insulation in first paragraph below. The most common jacket for ductwork and plenum applications is FSK.

        - Mineral-Fiber Board Insulation: Mineral or glass fibers bonded with a thermosetting resin. Comply with ASTM C 612, Type IA or Type IB. For duct and plenum applications, provide insulation [without factory-applied jacket] [with factory-applied ASJ] [with factory-applied FSK jacket]. Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - CertainTeed Corporation.

            - Johns Manville; a Berkshire Hathaway company.

            - Knauf Insulation.

            - Manson Insulation Inc.

            - Owens Corning.

            - <Insert manufacturer's name>.

Pipe and tank insulation is used for large-diameter piping and vessels. ASJ is commonly used.

        - Mineral-Fiber, Pipe and Tank Insulation: Mineral or glass fibers bonded with a thermosetting resin. Semirigid board material with factory-applied [ASJ] [FSK jacket] complying with ASTM C 1393, Type II or Type IIIA Category 2, or with properties similar to ASTM C 612, Type IB. Nominal density is 2.5 lb/cu. ft. (40 kg/cu. m) or more. Thermal conductivity (k-value) at 100 deg F (55 deg C) is 0.29 Btu x in./h x sq. ft. x deg F (0.042 W/m x K) or less. Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - CertainTeed Corporation.

            - Johns Manville; a Berkshire Hathaway company.

            - Knauf Insulation.

            - Manson Insulation Inc.

            - Owens Corning.

            - <Insert manufacturer's name>.

        - Polyolefin: Unicellular, polyethylene thermal plastic insulation. Comply with ASTM C 1427, Type I, Grade 1 for tubular materials and Type II, Grade 1 for sheet materials.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [Tubolit Sheet and Roll Foam Insulation] or a comparable product by one of the following:

            - <Insert manufacturer's name>.

      - FIRE-RATED INSULATION SYSTEMS

Retain this article for fire-rated insulation, which is sometimes used in lieu of fire-rated assemblies. A common application is for Type I, commercial, kitchen hood exhaust ductwork. See Evaluations.

        - Fire-Rated Board: Structural-grade, press-molded, xonolite calcium silicate, fireproofing board suitable for operating temperatures up to 1700 deg F (927 deg C). Comply with ASTM C 656, Type II, Grade 6. Tested and certified to provide a [1] [2]-hour fire rating by an NRTL acceptable to authorities having jurisdiction.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by the following:

            - Johns Manville; a Berkshire Hathaway company.

            - <Insert manufacturer's name>.

        - Fire-Rated Blanket: High-temperature, flexible, blanket insulation with FSK jacket that is tested and certified to provide a [1] [2]-hour fire rating by an NRTL acceptable to authorities having jurisdiction.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - 3M.

            - CertainTeed Corporation.

            - Johns Manville; a Berkshire Hathaway company.

            - Nelson Firestop; a brand of Emerson Industrial Automation.

            - Thermal Ceramics.

            - Unifrax Corporation.

            - <Insert manufacturer's name>.

      - ADHESIVES

Military Specification in this article was the only standard available when this Section was written. MIL-A-3316C was last updated in October 1987.

        - Materials shall be compatible with insulation materials, jackets, and substrates and for bonding insulation to itself and to surfaces to be insulated unless otherwise indicated.

        - Flexible Elastomeric and Polyolefin Adhesive: Comply with MIL-A-24179A, Type II, Class I.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [ArmaFlex 520 Adhesive] or a comparable product by one of the following:

            - Aeroflex USA, Inc.

            - Foster Brand; H. B. Fuller Construction Products.

            - K-Flex USA.

            - <Insert manufacturer's name>.

        - Flexible Elastomeric and Polyolefin Adhesive: Comply with SCAQMD Rule 1168.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

The following low VOC adhesives are suitable for LEED and other sustainable system requirements.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [ArmaFlex 520 Black Low VOC Adhesive] [or] [Low VOC Spray Adhesive] or a comparable product by one of the following:

            - Aeroflex USA, Inc.

            - Foster Brand; H. B. Fuller Construction Products.

            - K-Flex USA.

            - <Insert manufacturer's name>.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for plastic foam adhesives.

          - Adhesives shall have a VOC content of [50] <Insert value> g/L or less.

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

          - Adhesive shall comply with the testing and product requirements of the MAS Certified Green Program.

        - Flexible Elastomeric and Polyolefin Adhesive: High Temperature.

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

The following high temperature adhesive is for UT Solaflex.

          - Basis-of-Design Product: Subject to compliance with requirements, provide Armacell LLC; [HT 625 Insulation Adhesive] or a comparable product by one of the following:

            - Aeroflex USA, Inc.

            - Foster Brand; H. B. Fuller Construction Products.

            - K-Flex USA.

            - <Insert manufacturer's name>.

        - Mineral-Fiber Adhesive: Comply with MIL-A-3316C, Class 2, Grade A.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Childers Brand; H. B. Fuller Construction Products.

            - Eagle Bridges - Marathon Industries.

            - Foster Brand; H. B. Fuller Construction Products.

            - Mon-Eco Industries, Inc.

            - <Insert manufacturer's name>.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for fiberglass.

          - Fiberglass adhesive shall have a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

          - Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

        - ASJ Adhesive, and FSK Jacket Adhesive: Comply with MIL-A-3316C, Class 2, Grade A for bonding insulation jacket lap seams and joints.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Childers Brand; H. B. Fuller Construction Products.

            - Eagle Bridges - Marathon Industries.

            - Foster Brand; H. B. Fuller Construction Products.

            - Mon-Eco Industries, Inc.

            - <Insert manufacturer's name>.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for contact adhesive.

          - Adhesive shall have a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

          - Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

        - PVC Jacket Adhesive: Compatible with PVC jacket.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Dow Corning Corporation.

            - Johns Manville; a Berkshire Hathaway company.

            - P.I.C. Plastics, Inc.

            - Speedline Corporation.

            - <Insert manufacturer's name>.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for contact adhesive.

          - Adhesive shall have a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

          - Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

      - MASTICS

The industry does not have a clear definition that categorizes mastics into vapor barriers, vapor retarders, and breather mastics. Specification follows the nomenclature used by Foster. Products with a perm rating of 0.1 and lower are considered vapor barriers. Products with a perm rating greater than 0.1 and less than 1.0 are considered vapor retarders. Products with a perm rating greater than 1.0 are called "breathable." Consider ambient conditions and operating temperatures when selecting a mastic. Consider using water-based mastics for environmental reasons.

        - Materials shall be compatible with insulation materials, jackets, and substrates; comply with MIL-PRF-19565C, Type II.

"VOC Content" Subparagraph below applies to LEED 2009 NC, CI, and CS Credit IEQ 4.2.

          - VOC Content: [300] <Insert value> g/L or less.

"Low-Emitting Materials" Subparagraph below applies to LEED 2009 for Schools.

          - Low-Emitting Materials: Mastic coatings shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

Verify that products listed comply with water-vapor permeance. Require proof of performance and certified test reports from vapor-barrier mastic manufacturer to support product literature claims.

Retain one of four mastic paragraphs below. Product attributes in first paragraph are based on Foster; there are variations among manufacturers.

        - Vapor-Barrier Mastic: Water based; suitable for indoor use on below ambient services.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Childers Brand; H. B. Fuller Construction Products.

            - Foster Brand; H. B. Fuller Construction Products.

            - Knauf Insulation.

            - Vimasco Corporation.

            - <Insert manufacturer's name>.

          - Water-Vapor Permeance: ASTM E 96/E 96M, Procedure B, 0.013 perm (0.009 metric perm) at 43-mil (1.09-mm) dry film thickness.

          - Service Temperature Range: Minus 20 to plus 180 deg F (Minus 29 to plus 82 deg C).

          - Solids Content: ASTM D 1644, 58 percent by volume and 70 percent by weight.

          - Color: White.

        - Vapor-Barrier Mastic: Solvent based; suitable for indoor use on below ambient services.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Childers Brand; H. B. Fuller Construction Products.

            - Eagle Bridges - Marathon Industries.

            - Foster Brand; H. B. Fuller Construction Products.

            - Mon-Eco Industries, Inc.

            - <Insert manufacturer's name>.

          - Water-Vapor Permeance: ASTM F 1249, 0.05 perm (0.03 metric perm) at 35-mil (0.9-mm) dry film thickness.

          - Service Temperature Range: 0 to 180 deg F (Minus 18 to plus 82 deg C).

          - Solids Content: ASTM D 1644, 44 percent by volume and 62 percent by weight.

          - Color: White.

        - Vapor-Barrier Mastic: Solvent based; suitable for outdoor use on below ambient services.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Childers Brand; H. B. Fuller Construction Products.

            - Eagle Bridges - Marathon Industries.

            - Foster Brand; H. B. Fuller Construction Products.

            - <Insert manufacturer's name>.

          - Water-Vapor Permeance: ASTM F 1249, 0.05 perm (0.033 metric perm) at 30-mil (0.8-mm) dry film thickness.

          - Service Temperature Range: Minus 50 to plus 220 deg F (Minus 46 to plus 104 deg C).

          - Solids Content: ASTM D 1644, 33 percent by volume and 46 percent by weight.

          - Color: White.

        - Breather Mastic: Water based; suitable for indoor and outdoor use on above ambient services.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Childers Brand; H. B. Fuller Construction Products.

            - Eagle Bridges - Marathon Industries.

            - Foster Brand; H. B. Fuller Construction Products.

            - Knauf Insulation.

            - Mon-Eco Industries, Inc.

            - Vimasco Corporation.

            - <Insert manufacturer's name>.

          - Water-Vapor Permeance: ASTM F 1249, 1.8 perms (1.2 metric perms) at 0.0625-inch (1.6-mm) dry film thickness.

          - Service Temperature Range: Minus 20 to plus 180 deg F (Minus 29 to plus 82 deg C).

          - Solids Content: 60 percent by volume and 66 percent by weight.

          - Color: White.

      - LAGGING ADHESIVES

        - Description: Comply with MIL-A-3316C, Class I, Grade A and shall be compatible with insulation materials, jackets, and substrates.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Childers Brand; H. B. Fuller Construction Products.

            - Foster Brand; H. B. Fuller Construction Products.

            - Vimasco Corporation.

            - <Insert manufacturer's name>.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes. VOC content limit is that for adhesives for porous materials other than wood.

          - Adhesives shall have a VOC content of [50] <Insert value> g/L or less.

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

          - Adhesive shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

          - Fire-resistant, water-based lagging adhesive and coating for use indoors to adhere fire-resistant lagging cloths over duct insulation.

          - Service Temperature Range: 0 to plus 180 deg F (Minus 18 to plus 82 deg C).

          - Color: White.

      - SEALANTS

Materials in first paragraph below are for sealing metal jacket seams and joints.

        - FSK and Metal Jacket Flashing Sealants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Childers Brand; H. B. Fuller Construction Products.

            - Eagle Bridges - Marathon Industries.

            - Foster Brand; H. B. Fuller Construction Products.

            - Mon-Eco Industries, Inc.

            - <Insert manufacturer's name>.

          - Materials shall be compatible with insulation materials, jackets, and substrates.

          - Fire- and water-resistant, flexible, elastomeric sealant.

          - Service Temperature Range: Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C).

          - Color: Aluminum.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes.

          - Sealant shall have a VOC content of 420 g/L or less.

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

          - Sealant shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

        - ASJ Flashing Sealants, and Vinyl and PVC Jacket Flashing Sealants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by the following:

            - Childers Brand; H. B. Fuller Construction Products.

            - <Insert manufacturer's name>.

          - Materials shall be compatible with insulation materials, jackets, and substrates.

          - Fire- and water-resistant, flexible, elastomeric sealant.

          - Service Temperature Range: Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C).

          - Color: White.

Subparagraph below applies to LEED 2009 NC, CI, and CS; LEED v4; IgCC; ASHRAE 189.1; and Green Globes.

          - Sealant shall have a VOC content of 420 g/L or less.

Subparagraph below applies to LEED 2009 for Schools Credit IEQ 4.1.

          - Sealant shall comply with the testing and product requirements of the California Department of Public Health's "Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers."

      - FACTORY-APPLIED JACKETS

Coordinate types of factory-applied jacket insulation materials selected and types of factory-applied jackets indicated in insulation system schedules.

For insulation materials with factory-applied jackets for use on applications above 140 deg F (60 deg C), specify sufficient insulation thickness to maintain outer surface temperature of insulation below 140 deg F (60 deg C). 140 deg F (60 deg C) surface temperature is set by OSHA for personnel protection.

CertainTeed and Johns Manville offer a vinyl jacket, but it does not comply with ASTM C 1136. Knauf and Owens Corning do not offer a vinyl product.

        - Insulation system schedules indicate factory-applied jackets on various applications. When factory-applied jackets are indicated, comply with the following:

          - ASJ: White, kraft-paper, fiberglass-reinforced scrim with aluminum-foil backing; complying with ASTM C 1136, Type I.

          - ASJ-SSL: ASJ with self-sealing, pressure-sensitive, acrylic-based adhesive covered by a removable protective strip; complying with ASTM C 1136, Type I.

          - FSK Jacket: Aluminum-foil, fiberglass-reinforced scrim with kraft-paper backing; complying with ASTM C 1136, Type II.

          - Vinyl Jacket: White vinyl with a permeance of 1.3 perms (0.86 metric perm) when tested according to ASTM E 96/E 96M, Procedure A, and complying with NFPA 90A and NFPA 90B.

      - FIELD-APPLIED FABRIC-REINFORCING MESH

Both glass-fiber- and polyester-fabric-reinforcing meshes are acceptable.

Retain both paragraphs below to give Contractor option to use either glass-fiber or polyester fabric.

        - Woven Glass-Fiber Fabric: Approximately 6 oz./sq. yd. (203 g/sq. m) with a thread count of 5 strands by 5 strands/sq. in. (2 strands by 2 strands/sq. mm) for covering ducts.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by the following:

            - Childers Brand; H. B. Fuller Construction Products.

            - <Insert manufacturer's name>.

        - Woven Polyester Fabric: Approximately 1 oz./sq. yd. (34 g/sq. m) with a thread count of 10 strands by 10 strands/sq. in. (4 strands by 4 strands/sq. mm), in a Leno weave, for ducts.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Foster Brand; H. B. Fuller Construction Products.

            - Vimasco Corporation.

            - <Insert manufacturer's name>.

      - FIELD-APPLIED CLOTHS

        - Woven Glass-Fiber Fabric: Comply with MIL-C-20079H, Type I, plain weave, and presized a minimum of 8 oz./sq. yd. (271 g/sq. m).

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by the following:

            - Alpha Associates, Inc.

            - <Insert manufacturer's name>.

      - FIELD-APPLIED JACKETS

Insulation jackets in this article are for field application. ASTM C 921, Type I, is for use over insulation on ducts operating at below ambient temperatures at least part of the time or where a vapor barrier is required. ASTM C 921, Type II, is for use over insulation on ducts operating above ambient temperatures or where a vapor retarder is not required.

        - Field-applied jackets shall comply with ASTM C 921, Type I, unless otherwise indicated.

A properly sealed FSK jacket, common with most forms of factory-applied jackets for mineral-fiber insulation, complies with vapor-retarder requirements in ASTM C 921, Type I.

        - FSK Jacket: Aluminum-foil-face, fiberglass-reinforced scrim with kraft-paper backing.

Although other thicknesses for PVC jackets are available, a flame-spread index of 25 and a smoke-developed index of 50 apply only to thicknesses of 30 mils (0.8 mm) and less.

        - PVC Jacket: High-impact-resistant, UV-resistant PVC complying with ASTM D 1784, Class 16354-C; thickness as scheduled; roll stock ready for shop or field cutting and forming. Thickness is indicated in field-applied jacket schedules.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Johns Manville; a Berkshire Hathaway company.

            - P.I.C. Plastics, Inc.

            - Proto Corporation.

            - Speedline Corporation.

            - <Insert manufacturer's name>.

          - Adhesive: As recommended by jacket material manufacturer.

PVC jackets are available in several colors. Colored jackets may be used to replace field painting. UV rays fade colors in exterior applications. Some colors (black, gray, and white) do not fade as quickly as other colors (red, orange, and green). Colored jackets have different emissivity and are not recommended for outdoor use.

          - Color: [White] [Color-code jackets based on system. Color as selected by Architect].

        - Metal Jacket:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - ITW Insulation Systems; Illinois Tool Works, Inc.

            - RPR Products, Inc.

            - <Insert manufacturer's name>.

          - Aluminum Jacket: Comply with ASTM B 209 (ASTM B 209M), Alloy 3003, 3005, 3105, or 5005, Temper H-14.

            - [Sheet and roll stock ready for shop or field sizing] [Factory cut and rolled to size].

            - Finish and thickness are indicated in field-applied jacket schedules.

Among the three moisture barriers in first subparagraph below, 1-mil (0.025-mm) barrier provides the least protection against galvanic corrosion, 3-mil (0.075-mm) barrier offers better protection, and polysurlyn barrier offers the best protection. For most indoor applications, 1-mil (0.025-mm) barrier is adequate. For outdoor applications, select either 3-mil (0.075-mm) or polysurlyn barrier.

            - Moisture Barrier for Indoor Applications: [1-mil- (0.025-mm-) thick, heat-bonded polyethylene and kraft paper] [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick polysurlyn].

            - Moisture Barrier for Outdoor Applications: [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick polysurlyn].

          - Stainless-Steel Jacket: ASTM A 167 or ASTM A 240/A 240M.

            - [Sheet and roll stock ready for shop or field sizing] [Factory cut and rolled to size].

            - Material, finish, and thickness are indicated in field-applied jacket schedules.

Among the three moisture barriers in first subparagraph below, 1-mil (0.025-mm) barrier provides the least protection against galvanic corrosion, 3-mil (0.075-mm) barrier offers better protection, and polysurlyn barrier offers the best protection. For most indoor applications, 1-mil (0.025-mm) barrier is adequate.

            - Moisture Barrier for Indoor Applications: [1-mil- (0.025-mm-) thick, heat-bonded polyethylene and kraft paper] [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick polysurlyn].

            - Moisture Barrier for Outdoor Applications: [3-mil- (0.075-mm-) thick, heat-bonded polyethylene and kraft paper] [2.5-mil- (0.063-mm-) thick polysurlyn].

        - Self-Adhesive Outdoor Jacket: 60-mil- (1.5-mm-) thick, laminated vapor barrier and waterproofing membrane for installation over insulation located aboveground outdoors; consisting of a rubberized bituminous resin on a crosslaminated polyethylene film covered with [white] [stucco-embossed] aluminum-foil facing.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by the following:

            - Polyguard Products, Inc.

            - <Insert manufacturer's name>.

      - TAPES

Product performance is based on products manufactured by Venture Tape; there are slight variations among manufacturers.

        - ASJ Tape: White vapor-retarder tape matching factory-applied jacket with acrylic adhesive, complying with ASTM C 1136.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Avery Dennison Corporation, Specialty Tapes Division.

            - Compac Corporation.

            - Ideal Tape Co., Inc., an American Biltrite Company.

            - Knauf Insulation.

            - Venture Tape.

            - <Insert manufacturer's name>.

          - Width: 3 inches (75 mm).

          - Thickness: 11.5 mils (0.29 mm).

          - Adhesion: 90 ounces force/inch (1.0 N/mm) in width.

          - Elongation: 2 percent.

          - Tensile Strength: 40 lbf/inch (7.2 N/mm) in width.

          - ASJ Tape Disks and Squares: Precut disks or squares of ASJ tape.

        - FSK Tape: Foil-face, vapor-retarder tape matching factory-applied jacket with acrylic adhesive; complying with ASTM C 1136.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Avery Dennison Corporation, Specialty Tapes Division.

            - Compac Corporation.

            - Ideal Tape Co., Inc., an American Biltrite Company.

            - Knauf Insulation.

            - Venture Tape.

            - <Insert manufacturer's name>.

          - Width: 3 inches (75 mm).

          - Thickness: 6.5 mils (0.16 mm).

          - Adhesion: 90 ounces force/inch (1.0 N/mm) in width.

          - Elongation: 2 percent.

          - Tensile Strength: 40 lbf/inch (7.2 N/mm) in width.

          - FSK Tape Disks and Squares: Precut disks or squares of FSK tape.

        - PVC Tape: White vapor-retarder tape matching field-applied PVC jacket with acrylic adhesive; suitable for indoor and outdoor applications.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Compac Corporation.

            - Ideal Tape Co., Inc., an American Biltrite Company.

            - Venture Tape.

            - <Insert manufacturer's name>.

          - Width: 2 inches (50 mm).

          - Thickness: 6 mils (0.15 mm).

          - Adhesion: 64 ounces force/inch (0.7 N/mm) in width.

          - Elongation: 500 percent.

          - Tensile Strength: 18 lbf/inch (3.3 N/mm) in width.

        - Aluminum-Foil Tape: Vapor-retarder tape with acrylic adhesive.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - Avery Dennison Corporation, Specialty Tapes Division.

            - Compac Corporation.

            - Ideal Tape Co., Inc., an American Biltrite Company.

            - Knauf Insulation.

            - Venture Tape.

            - <Insert manufacturer's name>.

          - Width: 2 inches (50 mm).

          - Thickness: 3.7 mils (0.093 mm).

          - Adhesion: 100 ounces force/inch (1.1 N/mm) in width.

          - Elongation: 5 percent.

          - Tensile Strength: 34 lbf/inch (6.2 N/mm) in width.

      - SECUREMENTS

        - Bands:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

            - ITW Insulation Systems; Illinois Tool Works, Inc.

            - RPR Products, Inc.

            - <Insert manufacturer's name>.

Wing seals are primarily used for fastening bands together. Closed seals are occasionally used for large, 84-inch- (2130-mm-) diameter applications and where fastening bands are used with springs. Wing seals are reusable; closed seals are not.

          - Stainless Steel: ASTM A 167 or ASTM A 240/A 240M, [Type 304] [or] [Type 316]; 0.015 inch (0.38 mm) thick, [1/2 inch (13 mm)] [3/4 inch (19 mm)] wide with [wing seal] [or] [closed seal].

          - Aluminum: ASTM B 209 (ASTM B 209M), Alloy 3003, 3005, 3105, or 5005; Temper H-14, 0.020 inch (0.51 mm) thick, [1/2 inch (13 mm)] [3/4 inch (19 mm)] wide with [wing seal] [or] [closed seal].

Springs are used for large, 84-inch- (2130-mm-) diameter applications and on applications with rapid changes in expansion and contraction.

          - Springs: Twin spring set constructed of stainless steel with ends flat and slotted to accept metal bands. Spring size determined by manufacturer for application.

        - Insulation Pins and Hangers:

          - Capacitor-Discharge-Weld Pins: Copper- or zinc-coated steel pin, fully annealed for capacitor-discharge welding, [0.106-inch- (2.6-mm-)] [0.135-inch- (3.5-mm-)] diameter shank, length to suit depth of insulation indicated.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

            - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

              - AGM Industries, Inc.

              - Gemco.

              - Hardcast, Inc.

              - Midwest Fasteners, Inc.

              - Nelson Stud Welding.

              - <Insert manufacturer's name>.

          - Cupped-Head, Capacitor-Discharge-Weld Pins: Copper- or zinc-coated steel pin, fully annealed for capacitor-discharge welding, [0.106-inch- (2.6-mm-)] [0.135-inch- (3.5-mm-)] diameter shank, length to suit depth of insulation indicated with integral 1-1/2-inch (38-mm) galvanized carbon-steel washer.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

            - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

              - AGM Industries, Inc.

              - CL WARD & Family Inc.

              - Gemco.

              - Hardcast, Inc.

              - Midwest Fasteners, Inc.

              - Nelson Stud Welding.

              - <Insert manufacturer's name>.

          - Metal, Adhesively Attached, Perforated-Base Insulation Hangers: Baseplate welded to projecting spindle that is capable of holding insulation, of thickness indicated, securely in position indicated when self-locking washer is in place. Comply with the following requirements:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

            - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

              - AGM Industries, Inc.

              - Gemco.

              - Midwest Fasteners, Inc.

              - <Insert manufacturer's name>.

            - Baseplate: Perforated, galvanized carbon-steel sheet, 0.030 inch (0.76 mm) thick by 2 inches (50 mm) square.

            - Spindle: [Copper- or zinc-coated, low-carbon steel] [Aluminum] [Stainless steel], fully annealed, 0.106-inch- (2.6-mm-) diameter shank, length to suit depth of insulation indicated.

            - Adhesive: Recommended by hanger manufacturer. Product with demonstrated capability to bond insulation hanger securely to substrates indicated without damaging insulation, hangers, and substrates.

          - Nonmetal, Adhesively Attached, Perforated-Base Insulation Hangers: Baseplate fastened to projecting spindle that is capable of holding insulation, of thickness indicated, securely in position indicated when self-locking washer is in place. Comply with the following requirements:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

            - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

              - Gemco.

              - Midwest Fasteners, Inc.

              - <Insert manufacturer's name>.

            - Baseplate: Perforated, nylon sheet, 0.030 inch (0.76 mm) thick by 1-1/2 inches (38 mm) in diameter.

            - Spindle: Nylon, 0.106-inch- (2.6-mm-) diameter shank, length to suit depth of insulation indicated, up to 2-1/2 inches (63 mm).

            - Adhesive: Recommended by hanger manufacturer. Product with demonstrated capability to bond insulation hanger securely to substrates indicated without damaging insulation, hangers, and substrates.

          - Self-Sticking-Base Insulation Hangers: Baseplate welded to projecting spindle that is capable of holding insulation, of thickness indicated, securely in position indicated when self-locking washer is in place. Comply with the following requirements:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

            - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

              - AGM Industries, Inc.

              - Gemco.

              - Hardcast, Inc.

              - Midwest Fasteners, Inc.

              - <Insert manufacturer's name>.

            - Baseplate: Galvanized carbon-steel sheet, 0.030 inch (0.76 mm) thick by 2 inches (50 mm) square.

            - Spindle: [Copper- or zinc-coated, low-carbon steel] [Aluminum] [Stainless steel], fully annealed, 0.106-inch- (2.6-mm-) diameter shank, length to suit depth of insulation indicated.

            - Adhesive-backed base with a peel-off protective cover.

          - Insulation-Retaining Washers: Self-locking washers formed from 0.016-inch- (0.41-mm-) thick, [galvanized-steel] [aluminum] [stainless-steel] sheet, with beveled edge sized as required to hold insulation securely in place but not less than 1-1/2 inches (38 mm) in diameter.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. See Section 016000 "Product Requirements."

            - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

              - AGM Industries, Inc.

              - Gemco.

              - Hardcast, Inc.

              - Midwest Fasteners, Inc.

              - Nelson Stud Welding.

              - <Insert manufacturer's name>.

            - Protect ends with capped self-locking washers incorporating a spring steel insert to ensure permanent retention of cap in exposed locations.

          - Nonmetal Insulation-Retaining Washers: Self-locking washers formed from 0.016-inch- (0.41-mm-) thick nylon sheet, with beveled edge sized as required to hold insulation securely in place but not less than 1-1/2 inches (38 mm) in diameter.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

            - Manufacturers: Subject to compliance with requirements, provide products by one of the following:

              - Gemco.

              - Midwest Fasteners, Inc.

              - <Insert manufacturer's name>.

        - Staples: Outward-clinching insulation staples, nominal 3/4-inch- (19-mm-) wide, stainless steel or Monel.

In paragraph below, stainless steel is the most common wire used and is best suited for all applications.

        - Wire: [0.080-inch (2.0-mm) nickel-copper alloy] [0.062-inch (1.6-mm) soft-annealed, stainless steel] [0.062-inch (1.6-mm) soft-annealed, galvanized steel].

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

          - Manufacturers: Subject to compliance with requirements, provide products by the following:

            - C & F Wire.

            - <Insert manufacturer's name>.

      - CORNER ANGLES

        - PVC Corner Angles: [30 mils (0.8 mm)] <Insert dimension> thick, minimum 1 by 1 inch (25 by 25 mm), PVC according to ASTM D 1784, Class 16354-C. White or color-coded to match adjacent surface.

        - Aluminum Corner Angles: [0.040 inch (1.0 mm)] <Insert dimension> thick, minimum 1 by 1 inch (25 by 25 mm), aluminum according to ASTM B 209 (ASTM B 209M), Alloy 3003, 3005, 3105, or 5005; Temper H-14.

        - Stainless-Steel Corner Angles: [0.024 inch (0.61 mm)] <Insert dimension> thick, minimum 1 by 1 inch (25 by 25 mm), stainless steel according to ASTM A 167 or ASTM A 240/A 240M, [Type 304] [or] [Type 316].

- EXECUTION

      - EXAMINATION

        - Examine substrates and conditions for compliance with requirements for installation tolerances and other conditions affecting performance of insulation application.

          - Verify that systems to be insulated have been tested and are free of defects.

          - Verify that surfaces to be insulated are clean and dry.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PREPARATION

        - Surface Preparation: Clean and dry surfaces to receive insulation. Remove materials that will adversely affect insulation application.

      - GENERAL INSTALLATION REQUIREMENTS

        - Install insulation materials, accessories, and finishes with smooth, straight, and even surfaces; free of voids throughout the length of ducts and fittings.

        - Install insulation materials, vapor barriers or retarders, jackets, and thicknesses required for each item of duct system as specified in insulation system schedules.

        - Install accessories compatible with insulation materials and suitable for the service. Install accessories that do not corrode, soften, or otherwise attack insulation or jacket in either wet or dry state.

        - Install insulation with longitudinal seams at top and bottom of horizontal runs.

        - Install multiple layers of insulation with longitudinal and end seams staggered.

        - Keep insulation materials dry during application and finishing.

        - Install insulation with tight longitudinal seams and end joints. Bond seams and joints with adhesive recommended by insulation material manufacturer.

        - Install insulation with least number of joints practical.

        - Where vapor barrier is indicated, seal joints, seams, and penetrations in insulation at hangers, supports, anchors, and other projections with vapor-barrier mastic.

          - Install insulation continuously through hangers and around anchor attachments.

          - For insulation application where vapor barriers are indicated, extend insulation on anchor legs from point of attachment to supported item to point of attachment to structure. Taper and seal ends at attachment to structure with vapor-barrier mastic.

          - Install insert materials and install insulation to tightly join the insert. Seal insulation to insulation inserts with adhesive or sealing compound recommended by insulation material manufacturer.

        - Apply adhesives, mastics, and sealants at manufacturer's recommended coverage rate and wet and dry film thicknesses.

        - Install insulation with factory-applied jackets as follows:

          - Draw jacket tight and smooth.

          - Cover circumferential joints with 3-inch- (75-mm-) wide strips, of same material as insulation jacket. Secure strips with adhesive and outward clinching staples along both edges of strip, spaced 4 inches (100 mm) o.c.

          - Overlap jacket longitudinal seams at least 1-1/2 inches (38 mm). Clean and dry surface to receive self-sealing lap.

          - Cover joints and seams with tape, according to insulation material manufacturer's written instructions, to maintain vapor seal.

          - Where vapor barriers are indicated, apply vapor-barrier mastic on seams and joints and at ends adjacent to duct flanges and fittings.

        - Cut insulation in a manner to avoid compressing insulation more than 75 percent of its nominal thickness.

        - Finish installation with systems at operating conditions. Repair joint separations and cracking due to thermal movement.

        - Repair damaged insulation facings by applying same facing material over damaged areas. Extend patches at least 4 inches (100 mm) beyond damaged areas. Adhere, staple, and seal patches similar to butt joints.

      - PENETRATIONS

        - Insulation Installation at Roof Penetrations: Install insulation continuously through roof penetrations.

          - Seal penetrations with flashing sealant.

          - For applications requiring only indoor insulation, terminate insulation above roof surface and seal with joint sealant. For applications requiring indoor and outdoor insulation, install insulation for outdoor applications tightly joined to indoor insulation ends. Seal joint with joint sealant.

          - Extend jacket of outdoor insulation outside roof flashing at least 2 inches (50 mm) below top of roof flashing.

          - Seal jacket to roof flashing with flashing sealant.

        - Insulation Installation at Aboveground Exterior Wall Penetrations: Install insulation continuously through wall penetrations.

          - Seal penetrations with flashing sealant.

          - For applications requiring only indoor insulation, terminate insulation inside wall surface and seal with joint sealant. For applications requiring indoor and outdoor insulation, install insulation for outdoor applications tightly joined to indoor insulation ends. Seal joint with joint sealant.

          - Extend jacket of outdoor insulation outside wall flashing and overlap wall flashing at least 2 inches (50 mm).

          - Seal jacket to wall flashing with flashing sealant.

        - Insulation Installation at Interior Wall and Partition Penetrations (That Are Not Fire Rated): Install insulation continuously through walls and partitions.

        - Insulation Installation at Fire-Rated Wall and Partition Penetrations: Terminate insulation at fire damper sleeves for fire-rated wall and partition penetrations. Externally insulate damper sleeves to match adjacent insulation and overlap duct insulation at least 2 inches (50 mm).

          - Comply with requirements in Section 078413 "Penetration Firestopping."

        - Insulation Installation at Floor Penetrations:

          - Duct: For penetrations through fire-rated assemblies, terminate insulation at fire damper sleeves and externally insulate damper sleeve beyond floor to match adjacent duct insulation. Overlap damper sleeve and duct insulation at least 2 inches (50 mm).

          - Seal penetrations through fire-rated assemblies. Comply with requirements in Section 078413 "Penetration Firestopping."

      - INSTALLATION OF FLEXIBLE ELASTOMERIC AND POLYOLEFIN INSULATION

        - Installation shall follow the manufacturer's installation instructions or ASTM C 1710.

        - Seal longitudinal seams and end joints with manufacturer's recommended adhesive to eliminate openings in insulation that allow passage of air to surface being insulated.

        - Square and Rectangular Ducts and Plenums:

          - Provide a 1/4-inch (6.4-mm) more per side for a tight, compression fit.

          - Cut sheet insulation with the following dimensions:

            - Width of duct plus 1/4-inch (6.4-mm), one piece.

            - Height of duct plus 1/4-inch (6.4-mm), plus thickness of insulation, two pieces.

            - Width of duct plus 1/4-inch (6.4-mm), plus two times the thickness of insulation, one piece.

          - Insulate the bottom of the duct with the sheet from (a) above, then the sides with the two sheets from (b) above, and finally the top of the duct with the sheet from (c) above.

          - Insulation without self-adhering backing:

            - Apply 100 percent coverage of manufacturer adhesive on the metal surface, then the insulation, except for the last 1/4-inch (6.4-mm) where sheets will butt together.

            - Roll sheet down into position.

            - Press two sheets together under compression and apply adhesive at the butt joint to seal the two sheets together.

          - Insulation with self-adhering backing:

            - Peel back release paper in 6- to 8-inch (150- to 203-mm) increments and line up sheet.

            - Press firmly to activate adhesive

            - Align material and continue to line up correctly, pressing firmly while slowly removing release paper.

            - Allow 1/4-inch (6.4-mm) overlap for compression at butt joints.

            - Apply Adhesive at the butt joint to seal the two sheets together.

          - Insulate duct brackets following manufacturer's written installation instructions.

        - Circular Ducts:

          - Determine the circumference of the duct, using a strip of insulation the same thickness as to be used.

          - Cut the sheet to the required size.

          - Apply 100 percent coverage of manufacturer adhesive on the metal surface then the insulation

          - Apply manufacturer adhesive to the cut surfaces along 100 percent of the longitudinal seam. Press together the seam at the ends and then the middle. Close the entire seam starting from the middle.

      - INSTALLATION OF MINERAL-FIBER INSULATION

        - Blanket Insulation Installation on Ducts and Plenums: Secure with adhesive and insulation pins.

In first subparagraph below, many manufacturers do not recommend 100 percent coverage of adhesive because of the effect on the overall insulation system's fire-performance characteristics. Verify application coverage recommendations with insulation manufacturer.

          - Apply adhesives according to manufacturer's recommended coverage rates per unit area, for [100] [50] <Insert number> percent coverage of duct and plenum surfaces.

Revise first subparagraph below to allow adhesive to be omitted from top surface of horizontal rectangular ducts.

          - Apply adhesive to entire circumference of ducts and to all surfaces of fittings and transitions.

          - Install either capacitor-discharge-weld pins and speed washers or cupped-head, capacitor-discharge-weld pins on sides and bottom of horizontal ducts and sides of vertical ducts as follows:

            - On duct sides with dimensions 18 inches (450 mm) and smaller, place pins along longitudinal centerline of duct. Space 3 inches (75 mm) maximum from insulation end joints, and 16 inches (400 mm) o.c.

            - On duct sides with dimensions larger than 18 inches (450 mm), place pins 16 inches (400 mm) o.c. each way, and 3 inches (75 mm) maximum from insulation joints. Install additional pins to hold insulation tightly against surface at cross bracing.

            - Pins may be omitted from top surface of horizontal, rectangular ducts and plenums.

            - Do not overcompress insulation during installation.

            - Impale insulation over pins and attach speed washers.

            - Cut excess portion of pins extending beyond speed washers or bend parallel with insulation surface. Cover exposed pins and washers with tape matching insulation facing.

          - For ducts and plenums with surface temperatures below ambient, install a continuous unbroken vapor barrier. Create a facing lap for longitudinal seams and end joints with insulation by removing 2 inches (50 mm) from one edge and one end of insulation segment. Secure laps to adjacent insulation section with 1/2-inch (13-mm) outward-clinching staples, 1 inch (25 mm) o.c. Install vapor barrier consisting of factory- or field-applied jacket, adhesive, vapor-barrier mastic, and sealant at joints, seams, and protrusions.

            - Repair punctures, tears, and penetrations with tape or mastic to maintain vapor-barrier seal.

            - Install vapor stops for ductwork and plenums operating below 50 deg F (10 deg C) at 18-foot (5.5-m) intervals. Vapor stops shall consist of vapor-barrier mastic applied in a Z-shaped pattern over insulation face, along butt end of insulation, and over the surface. Cover insulation face and surface to be insulated a width equal to two times the insulation thickness, but not less than 3 inches (75 mm).

          - Overlap unfaced blankets a minimum of 2 inches (50 mm) on longitudinal seams and end joints. At end joints, secure with steel bands spaced a maximum of 18 inches (450 mm) o.c.

          - Install insulation on rectangular duct elbows and transitions with a full insulation section for each surface. Install insulation on round and flat-oval duct elbows with individually mitered gores cut to fit the elbow.

          - Insulate duct stiffeners, hangers, and flanges that protrude beyond insulation surface with 6-inch- (150-mm-) wide strips of same material used to insulate duct. Secure on alternating sides of stiffener, hanger, and flange with pins spaced 6 inches (150 mm) o.c.

        - Board Insulation Installation on Ducts and Plenums: Secure with adhesive and insulation pins.

In first subparagraph below, many manufacturers do not recommend 100 percent coverage of adhesive because of the effect on the overall insulation system's fire-performance characteristics. Verify application coverage recommendations with insulation manufacturer.

          - Apply adhesives according to manufacturer's recommended coverage rates per unit area, for [100] [50] <Insert number> percent coverage of duct and plenum surfaces.

Revise first subparagraph below to allow adhesive to be omitted from top surface of horizontal rectangular ducts.

          - Apply adhesive to entire circumference of ducts and to all surfaces of fittings and transitions.

          - Install either capacitor-discharge-weld pins and speed washers or cupped-head, capacitor-discharge-weld pins on sides and bottom of horizontal ducts and sides of vertical ducts as follows:

            - On duct sides with dimensions 18 inches (450 mm) and smaller, place pins along longitudinal centerline of duct. Space 3 inches (75 mm) maximum from insulation end joints, and 16 inches (400 mm) o.c.

            - On duct sides with dimensions larger than 18 inches (450 mm), space pins 16 inches (400 mm) o.c. each way, and 3 inches (75 mm) maximum from insulation joints. Install additional pins to hold insulation tightly against surface at cross bracing.

            - Pins may be omitted from top surface of horizontal, rectangular ducts and plenums.

            - Do not overcompress insulation during installation.

            - Cut excess portion of pins extending beyond speed washers or bend parallel with insulation surface. Cover exposed pins and washers with tape matching insulation facing.

          - For ducts and plenums with surface temperatures below ambient, install a continuous unbroken vapor barrier. Create a facing lap for longitudinal seams and end joints with insulation by removing 2 inches (50 mm) from one edge and one end of insulation segment. Secure laps to adjacent insulation section with 1/2-inch (13-mm) outward-clinching staples, 1 inch (25 mm) o.c. Install vapor barrier consisting of factory- or field-applied jacket, adhesive, vapor-barrier mastic, and sealant at joints, seams, and protrusions.

            - Repair punctures, tears, and penetrations with tape or mastic to maintain vapor-barrier seal.

            - Install vapor stops for ductwork and plenums operating below 50 deg F (10 deg C) at 18-foot (5.5-m) intervals. Vapor stops shall consist of vapor-barrier mastic applied in a Z-shaped pattern over insulation face, along butt end of insulation, and over the surface. Cover insulation face and surface to be insulated a width equal to two times the insulation thickness, but not less than 3 inches (75 mm).

          - Install insulation on rectangular duct elbows and transitions with a full insulation section for each surface. Groove and score insulation to fit as closely as possible to outside and inside radius of elbows. Install insulation on round and flat-oval duct elbows with individually mitered gores cut to fit the elbow.

          - Insulate duct stiffeners, hangers, and flanges that protrude beyond insulation surface with 6-inch- (150-mm-) wide strips of same material used to insulate duct. Secure on alternating sides of stiffener, hanger, and flange with pins spaced 6 inches (150 mm) o.c.

      - FIELD-APPLIED JACKET INSTALLATION

        - Where glass-cloth jackets are indicated, install directly over bare insulation or insulation with factory-applied jackets.

          - Draw jacket smooth and tight to surface with 2-inch (50-mm) overlap at seams and joints.

          - Embed glass cloth between two 0.062-inch- (1.6-mm-) thick coats of lagging adhesive.

          - Completely encapsulate insulation with coating, leaving no exposed insulation.

        - Where FSK jackets are indicated, install as follows:

          - Draw jacket material smooth and tight.

          - Install lap or joint strips with same material as jacket.

          - Secure jacket to insulation with manufacturer's recommended adhesive.

          - Install jacket with 1-1/2-inch (38-mm) laps at longitudinal seams and 3-inch- (75-mm-) wide joint strips at end joints.

          - Seal openings, punctures, and breaks in vapor-retarder jackets and exposed insulation with vapor-barrier mastic.

        - Where PVC jackets are indicated, install with 1-inch (25-mm) overlap at longitudinal seams and end joints; for horizontal applications, install with longitudinal seams along top and bottom of tanks and vessels. Seal with manufacturer's recommended adhesive.

          - Apply two continuous beads of adhesive to seams and joints, one bead under lap and the finish bead along seam and joint edge.

        - Where metal jackets are indicated, install with 2-inch (50-mm) overlap at longitudinal seams and end joints. Overlap longitudinal seams arranged to shed water. Seal end joints with weatherproof sealant recommended by insulation manufacturer. Secure jacket with stainless-steel bands 12 inches (300 mm) o.c. and at end joints.

      - FIRE-RATED INSULATION SYSTEM INSTALLATION

        - Where fire-rated insulation system is indicated, secure system to ducts and duct hangers and supports to maintain a continuous fire rating.

        - Insulate duct access panels and doors to achieve same fire rating as duct.

        - Install firestopping at penetrations through fire-rated assemblies. Fire-stop systems are specified in Section 078413 "Penetration Firestopping."

      - FINISHES

Coordinate first paragraph below with Section 099113 "Exterior Painting" and Section 099123 "Interior Painting." If PVC jackets are specified, consult jacket manufacturers to determine suitable paint products and revise painting Sections to suit Project.

        - Insulation with ASJ, Glass-Cloth, or Other Paintable Jacket Material: Paint jacket with paint system identified below and as specified in Section 099113 "Exterior Painting" and Section 099123 "Interior Painting."

Retain paint system in subparagraphs below for a flat, latex-emulsion size over insulation covering an exterior that is subject to normal use and moderate environments.

          - Flat Acrylic Finish: [Two] <Insert number> finish coats over a primer that is compatible with jacket material and finish coat paint. Add fungicidal agent to render fabric mildew proof.

            - Finish Coat Material: Interior, flat, latex-emulsion size.

        - Flexible Elastomeric Thermal Insulation: After adhesive has fully cured, apply two coats of insulation manufacturer's recommended protective coating.

        - Color: Final color as selected by Architect. Vary first and second coats to allow visual inspection of the completed Work.

        - Do not field paint aluminum or stainless-steel jackets.

      - FIELD QUALITY CONTROL

Inspections in this article are destructive. Retain if workmanship quality is an important requirement. Architect should be prepared to reject all work if defective work is discovered in sample inspection.

Retain one of first two paragraphs below to identify who shall perform tests and inspections. If retaining second option in first paragraph, or if retaining second paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

        - Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain first paragraph below to require Contractor to perform tests and inspections.

        - Perform tests and inspections.

Retain first paragraph below to describe tests and inspections to be performed.

        - Tests and Inspections:

          - Inspect ductwork, randomly selected by Architect, by removing field-applied jacket and insulation in layers in reverse order of their installation. Extent of inspection shall be limited to [one] <Insert number> location(s) for each duct system defined in the "Duct Insulation Schedule, General" Article.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - All insulation applications will be considered defective Work if sample inspection reveals noncompliance with requirements.

Materials and thicknesses in schedules below are for single-layer applications. If multilayer applications are needed, insert additional requirements.

      - DUCT INSULATION SCHEDULE, GENERAL

        - Plenums and Ducts Requiring Insulation:

          - Indoor, concealed supply and outdoor air.

          - Indoor, exposed supply and outdoor air.

          - Indoor, concealed return located in unconditioned space.

          - Indoor, exposed return located in unconditioned space.

          - Indoor, concealed, Type I, commercial, kitchen hood exhaust.

          - Indoor, exposed, Type I, commercial, kitchen hood exhaust.

          - Indoor, concealed oven and warewash exhaust.

          - Indoor, exposed oven and warewash exhaust.

          - Indoor, concealed exhaust between isolation damper and penetration of building exterior.

          - Indoor, exposed exhaust between isolation damper and penetration of building exterior.

          - Outdoor, concealed supply and return.

          - Outdoor, exposed supply and return.

        - Items Not Insulated:

          - Fibrous-glass ducts.

          - Metal ducts with duct liner of sufficient thickness to comply with energy code and ASHRAE/IESNA 90.1.

          - Factory-insulated flexible ducts.

          - Factory-insulated plenums and casings.

          - Flexible connectors.

          - Vibration-control devices.

          - Factory-insulated access panels and doors.

Duct and plenum insulation schedules in first two articles below specify commonly used insulation materials and thicknesses for each service type. LEED Prerequisite EA 2 requires that duct insulation R-value comply with ASHRAE/IESNA 90.1 tables titled "Minimum Duct Insulation R-Value, Cooling and Heating Only Supply Ducts and Return Ducts" and "Minimum Duct Insulation R-Value, Combined Heating and Cooling Supply Ducts and Return Ducts." Not all materials and thicknesses may be suitable for a specific project. Revise to suit Project after considering all parameters that impact selection. Do not duplicate requirements inserted in "Insulation Materials" Article. See Evaluations for more information and guidance.

Polyolefin thickness is limited to 1 inch (25 mm) to meet a flame-spread index of 25 and a smoke-developed index of 50. Condensation control and energy efficiency are limited by thickness.

Consider the exposure of installed insulation to damage. Concealed applications have less risk than exposed.

      - INDOOR DUCT AND PLENUM INSULATION SCHEDULE

See the Insulation Evaluation tables in the Evaluations for rankings of different insulation types for different service ranges.

Retain one or more options in paragraphs below to allow Contractor to select insulation materials from those retained.

        - Concealed, round and flat-oval, supply-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Concealed, round and flat-oval, return-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Concealed, round and flat-oval, outdoor-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Concealed, round and flat-oval, exhaust-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Concealed, rectangular, supply-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Concealed, rectangular, return-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Concealed, rectangular, outdoor-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Concealed, rectangular, exhaust-air duct insulation between isolation damper and penetration of building exterior shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Concealed, Type I, Commercial, Kitchen Hood Exhaust Duct and Plenum Insulation: Fire-rated [blanket] [or] [board]; thickness as required to achieve 2-hour fire rating.

        - Concealed, supply-air plenum insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Concealed, return-air plenum insulation shall be[ one of] the following:

          - Flexible Elastomeric: [1 inch (25 mm)] <Insert dimension> thick.

        - Concealed, outdoor-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

          - Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

        - Concealed, exhaust-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

          - Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

        - Exposed, round and flat-oval, supply-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Exposed, round and flat-oval, return-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Exposed, round and flat-oval, outdoor-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Exposed, round and flat-oval, exhaust-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Exposed, rectangular, supply-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Exposed, rectangular, return-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Exposed, rectangular, outdoor-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Exposed, rectangular, exhaust-air duct insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Exposed, Type I, Commercial, Kitchen Hood Exhaust Duct and Plenum Insulation: Fire-rated [blanket] [or] [board]; thickness as required to achieve 2-hour fire rating.

        - Exposed, supply-air plenum insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Exposed, return-air plenum insulation shall be[ one of] the following:

          - Flexible Elastomeric: [2 inches (50 mm)] <Insert dimension> thick.

        - Exposed, outdoor-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

          - Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

        - Exposed, exhaust-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Mineral-Fiber Blanket: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [0.75-lb/cu. ft. (12-kg/cu. m)] [1.5-lb/cu. ft. (24-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] nominal density.

          - Mineral-Fiber Board: [1-1/2 inches (38 mm)] [2 inches (50 mm)] [3 inches (75 mm)] <Insert dimension> thick and [2-lb/cu. ft. (32-kg/cu. m)] [3-lb/cu. ft. (48-kg/cu. m)] [6-lb/cu. ft. (96-kg/cu. m)] nominal density.

      - ABOVEGROUND, OUTDOOR DUCT AND PLENUM INSULATION SCHEDULE

See the Insulation Evaluation tables in the Evaluations for rankings of different insulation types for different service ranges.

Retain one or more options in paragraphs below to allow Contractor to select insulation materials from those retained.

To comply with ASHRAE/IESNA 90.1, insulation should have an R-value of 8 or higher.

        - Insulation materials and thicknesses are identified below. If more than one material is listed for a duct system, selection from materials listed is Contractor's option.

        - Concealed, round and flat-oval, supply-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Flexible Elastomeric <with factory-applied jacket>: [2 inches (50 mm)] <Insert dimension> thick.

          - Polyolefin: [2-1/2 inches (64 mm)] <Insert dimension> thick.

        - Concealed, round and flat-oval, return-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Flexible Elastomeric <with factory-applied jacket>: [2 inches (50 mm)] <Insert dimension> thick.

          - Polyolefin: [2-1/2 inches (64 mm)] <Insert dimension> thick.

        - Concealed, round and flat-oval, outdoor-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Flexible Elastomeric <with factory-applied jacket>: [2 inches (50 mm)] <Insert dimension> thick.

          - Polyolefin: [2-1/2 inches (64 mm)] <Insert dimension> thick.

        - Concealed, rectangular, supply-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Flexible Elastomeric <with factory-applied jacket>: [2 inches (50 mm)] <Insert dimension> thick.

          - Polyolefin: [2-1/2 inches (64 mm)] <Insert dimension> thick.

        - Concealed, rectangular, return-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Flexible Elastomeric <with factory-applied jacket>: [2 inches (50 mm)] <Insert dimension> thick.

          - Polyolefin: [2-1/2 inches (64 mm)] <Insert dimension> thick.

        - Concealed, supply-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Flexible Elastomeric <with factory-applied jacket>: [2 inches (50 mm)] <Insert dimension> thick.

          - Polyolefin: [2-1/2 inches (64 mm)] <Insert dimension> thick.

        - Concealed, return-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Flexible Elastomeric <with factory-applied jacket>: [2 inches (50 mm)] <Insert dimension> thick.

          - Polyolefin: [2-1/2 inches (50 mm)] <Insert dimension> thick.

        - Exposed, round and flat-oval, supply-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Flexible Elastomeric : [2 inches (50 mm)] <Insert dimension> thick.

          - Polyolefin: [2-1/2 inches (64 mm)] <Insert dimension> thick.

        - Exposed, round and flat-oval, return-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Flexible Elastomeric : [2 inches (50 mm)] <Insert dimension> thick.

          - Polyolefin: [2-1/2 inches (64 mm)] <Insert dimension> thick.

        - Exposed, rectangular, supply-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Flexible Elastomeric <with factory-applied jacket>: [2 inches (50 mm)] <Insert dimension> thick.

          - Polyolefin: [2-1/2 inches (64 mm)] <Insert dimension> thick.

        - Exposed, rectangular, return-air duct insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Flexible Elastomeric <with factory-applied jacket>: [2 inches (50 mm)] <Insert dimension> thick.

          - Polyolefin: [2-1/2 inches (64 mm)] <Insert dimension> thick.

        - Exposed, supply-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Flexible Elastomeric <with factory-applied jacket>: [2 inches (50 mm)] <Insert dimension> thick.

          - Polyolefin: [2-1/2 inches (64 mm)] <Insert dimension> thick.

        - Exposed, return-air plenum insulation shall be[ one of] the following:

Retain one or both subparagraphs below.

          - Flexible Elastomeric <with factory-applied jacket>: [2 inches (50 mm)] <Insert dimension> thick.

          - Polyolefin: [2-1/2 inches (64 mm)] <Insert dimension> thick.

      - INDOOR, FIELD-APPLIED JACKET SCHEDULE

Possible variations of jackets by location are endless. This article specifies locations in two broad categories: concealed and exposed. Revise if additional delineation is necessary.

        - Install jacket over insulation material. For insulation with factory-applied jacket, install the field-applied jacket over the factory-applied jacket.

        - If more than one material is listed, selection from materials listed is Contractor's option.

        - Ducts and Plenums, Concealed:

Retain one of six subparagraphs below.

          - None.

          - [PVC] [PVC, Color-Coded by System]: [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

          - Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

          - Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

          - Stainless Steel, [Type 304] [or] [Type 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]: [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

          - <Insert jacket type>.

        - Ducts and Plenums, Exposed:

Retain one of six subparagraphs below.

          - None.

          - [PVC] [PVC, Color-Coded by System]: [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

          - Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

          - Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

          - Stainless Steel, [Type 304] [or] [Type 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]: [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

          - <Insert jacket type>.

      - OUTDOOR, FIELD-APPLIED JACKET SCHEDULE

Possible variations of jackets by location are endless. This article specifies locations in two broad categories: concealed and exposed. Revise if additional delineation is necessary.

30-mil (0.8-mm) or heavier PVC is recommended for outdoor applications. 40-mil (1.0-mm) PVC does not meet a flame-spread index of 25 and a smoke-developed index of 50; however, a flame-spread or smoke-developed index is not a requirement for outdoor applications.

0.024-inch (0.61-mm) or heavier aluminum is recommended for outdoor applications.

Painted aluminum increases surface emissivity and provides added chemical resistance. See Evaluations for discussion of emissivity.

0.016-inch (0.41-mm) or heavier stainless steel is recommended for outdoor applications.

Z-shaped locking seam is recommended for metal jackets located in unprotected applications that are exposed to severe weather.

        - Install jacket over insulation material. For insulation with factory-applied jacket, install the field-applied jacket over the factory-applied jacket.

        - If more than one material is listed, selection from materials listed is Contractor's option.

        - Ducts and Plenums, Concealed:

Retain one of six subparagraphs below.

          - None.

          - [PVC] [PVC, Color-Coded by System]: [20 mils (0.5 mm)] [30 mils (0.8 mm)] thick.

          - Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

          - Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

          - Stainless Steel, [Type 304] [or] [Type 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]: [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

          - <Insert jacket type>.

        - Ducts and Plenums, Exposed, up to 48 Inches (1200 mm) in Diameter or with Flat Surfaces up to 72 Inches (1800 mm):

Retain one of four subparagraphs below.

          - Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

          - Painted Aluminum, [Smooth] [Corrugated] [Stucco Embossed]: [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] [0.032 inch (0.81 mm)] thick.

          - Stainless Steel, [Type 304] [or] [Type 316], [Smooth 2B Finish] [Corrugated] [Stucco Embossed]: [0.010 inch (0.25 mm)] [0.016 inch (0.41 mm)] [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

          - <Insert jacket type>.

        - Ducts and Plenums, Exposed, Larger Than 48 Inches (1200 mm) in Diameter or with Flat Surfaces Larger Than 72 Inches (1800 mm):

Retain one of three subparagraphs below.

          - [Painted ]Aluminum, [Smooth] [Stucco Embossed] with [1-1/4-Inch- (32-mm-) Deep Corrugations] [2-1/2-Inch- (65-mm-) Deep Corrugations] [4-by-1-Inch (100-by-25-mm) Box Ribs]: [0.032 inch (0.81 mm)] [0.040 inch (1.0 mm)] thick.

          - Stainless Steel, [Type 304] [or] [Type 316], [Smooth] [Stucco Embossed], with [1-1/4-Inch- (32-mm-) Deep Corrugations] [2-1/2-Inch- (65-mm-) Deep Corrugations] [4-by-1-Inch (100-by-25-mm) Box Ribs]: [0.020 inch (0.51 mm)] [0.024 inch (0.61 mm)] thick.

          - <Insert jacket type>.

END OF SECTION 230713