## Sheet1
PA Technology Center -- Heat Loss Through the Building Envelope
General Assumptions
Windy Night
Summary Performance
Radiative Losses |  |  |  | 369550.247 | (BTU/hr)
Conductive Losses |  |  |  | 132949.5931
Infiltration / Exfiltration |  |  |  | 6674.9375
Total Heat Loss Through the Envelope |  |  |  | 509174.7776 | (BTU/hr)
Given Data
Building Size: 400' x 150' plan, 10.5' story height
Inside RH = 50%
Outside RH = 20%
Looked-up data
Data |  |  |  |  | Source
Tout = |  | 12 | oF |  | Table 2, p HE-16
Tin = |  | 75 | oF |  | Table 1.6, p CF 4a
::
Radiative Losses (Sky and Nearby Woods)
Q = A*E*Gamma*(Tf^4 - Tsky^4) (BTU/hr)
A = Area of surface (facade or roof)
E = Emmisivity of surface (per Table 1, p HE 16)
Gamma= Steffan-Boltz constant
= 0.17x10-8 BTU/(hr*ft^2*oR^4)
= 5.7x10-8 W/(m^2*oK^4)
Tf = Temp of exterior surface of facade (oR = oF + 460; = Tout)
Tsky = Temp of sky (oR = oF + 460; per fig 14 and table 3, p HE 17
Calculations
Object | Area | E | Tf | Tsky | Q
| (SF) |  | (oF) | (oF) | (BTU/hr)
Roof | 60000 | 0.8 | 6 | -4 | 319818.8164
Glass | 3300 | 0.8 | 6 | -1 | 12432.8577
Panels | 9900 | 0.8 | 6 | -1 | 37298.573
Qtot | [5 empty] | 369550.247 | (BTU/hr)
Notes/Assumptions:
Floor assumed to be in Radiative Equilibrium with Ground
::
::
Conduction
Thru Facade, floor, roof |  | Q = A*(Tin-Tout)/Rtot
Rtot = R1+...+Rn (P HE 20 to HE 25)
| Parallel Mat'ls*: | R = Atot/(A1/R1 + ... + An/Rn)
*Assumption for R calculation, Parallel Mat'ls
All heat flow in vertical direction, and none in horizontal direction
Calculations - Facade, Roof, Floor
Location | Area | Rtot | Tout | Tin | Q
| (SF) | (ft^2*hr*oF/ | (oF) | (oF) | (BTU/hr)
BTU)
Roof | 1540 | 8.49 | 6 | 72 | 11971.7314
Walls | 1556 | 1.8 | 6 | 72 | 57053.3333
Floor | 1540 | 1.59 | 6 | 72 | 63924.5283
Qtot | [5 empty] | 132949.5931 | (BTU/hr)
Notes/Assumptions:
All heat flow in roof/floor/walls in perpendicular direction
Air in roof assumed to be still (no convective heat transfer)
Beams modeled as 1/2 inch by 12 inch recangles
::
Air Change
Temperature Induced
Q = C*CFH*(Tin-Tout)
C = Heat capacity of air (0.02 BTU / (ft^3oF)
CFH = cubic ft / hr of air entering the building by infiltration (P HE 9)
Humidity Induced
Q = Cp*CFH*(AHin - AHout)
Cp = Heat of vaporization of H20 [(0.0113 BTU / Grain) * (Lbs / ft^3)]
CFH = cubic ft / hr of air entering the building by infiltration
AHin, AHout = absolute humidity in and outside (Grains/Lbs; P HE 8)
Calculations - Temperature
Air change rate = |  | 0.5 | Air changes per hour
CFH = Building Volume * Air change rate / 2
Building Volume = |  | 14630
CFH = |  | 3657.5 | Cubic feet per hour
Q = C*CFH*(Tin-Tout)
Q = |  |  |  |  | 4608.45 | BTU/hr
Calculations - Humidity
CFH = |  | 3657.5 | Cubic feet per hour
AHin = |  | 55 | Grains / Lb
AHout = |  | 5 | Grains / Lb
Q = Cp*CFH*(AHin - AHout)
Q = |  |  |  |  | 2066.4875 | BTU/hr
Qtot: | [5 empty] | 6674.9375 | (BTU/hr)
Notes/Assumptions
No inflitration through roof or floor
No ventilation except by infiltration
Total Heat Loss (Radiation, Conduction, Infiltration) | [5 empty] | 509174.7776 | BTU/hr